Block Taxonomy and Component Register

Grid Scale Battery Energy Storage System |  Standard Product Platform

Document BX-SE-TAX-014  |  Rev 3

This register defines every block type that appears on a site single-line block diagram for the standard containerized BESS platform. It gives the function, tag convention, port complement, and the quantity rule for each block type. It does NOT define how blocks interconnect; interconnect and harness rules are held separately in the Interconnect and Harness Schedule (BX-SE-ICD-021).

CONFIDENTIAL - INTERNAL ENGINEERING

1   Platform Architecture

The platform is organized into a shared site section and a repeating power block. The site section is common to every project and is built once regardless of how many power blocks the project carries. The power block is the unit of scale: a project is quoted as a number of power blocks, and every power block is identical in its internal makeup.

Each power block carries one power conversion system, one DC combiner, and a fixed complement of four battery racks. Every battery rack has its own rack battery management unit. The site section carries the site controller, the auxiliary transformer, the medium-voltage step-up transformer, revenue metering, and the AC collection bus. One further site block, the AC combiner panel, is fitted only on larger builds; see its entry below for the fitment rule.

Tag convention: site blocks carry a fixed tag. Power-block equipment is numbered by power block. Where a block repeats inside a power block (racks and their BMS), the tag carries the power block number and then the position within the block. So the third rack in power block two is RK-2-3, and its management unit is BMS-2-3. Power conversion systems and DC combiners are numbered by power block only, zero-padded to two digits, for example PCS-02 and DCC-02.

2   Site Blocks (built once per site)

| Block type | Tag | Function | Ports | Qty rule |
| --- | --- | --- | --- | --- |
| Site Controller | SC-01 | Plant controller and SCADA gateway. Aggregates telemetry, dispatches setpoints. | COMMS (uplinks in), AUX-24V (in) | One per site |
| Aux Transformer | AUX-XFMR | Derives regulated 24 V control power for the site from the collection bus. | AUX-24V (out, multiple) | One per site |
| MV Step-up Transformer | MV-XFMR | Steps the collection voltage up to the medium-voltage point of interconnect. | AC-PWR (in) | One per site |
| Revenue Metering | MTR-01 | Revenue-grade metering at the point of common coupling. | AC-PWR (in, out), COMMS (out) | One per site |
| AC Collection Bus | AC-BUS | Low-voltage AC lineup that collects the power-block feeders. Four feeder positions. | AC-PWR (in x4, out) | One per site |
| AC Combiner Panel | AC-CMB | Aggregates surplus power-block feeders into a single bus feeder when the site exceeds the bus feeder count. | AC-PWR (in multiple, out one) | Fitted only when the site has more power blocks than the AC collection bus has feeder positions; otherwise omitted |

3   Power Block Equipment (repeats per power block)

A power block is the repeating unit. Every power block is identical: one PCS, one DC combiner, four battery racks, and one rack BMS per rack. There are no partial power blocks.

| Block type | Tag pattern | Function | Ports | Qty per power block |
| --- | --- | --- | --- | --- |
| Power Conversion System | PCS-nn | Bidirectional inverter for the power block. AC side to collection, DC side to the combiner. | DC-PWR (in), AC-PWR (out), COMMS (in from block, out to site), AUX-24V (in) | One |
| DC Combiner | DCC-nn | Combines four incoming rack DC feeds onto a single DC output. | DC-PWR (in x4, out), AUX-24V (in) | One |
| Battery Rack | RK-n-k | Energy storage rack. Presents a single DC power output. | DC-PWR (out) | Four |
| Rack BMS | BMS-n-k | Rack management and protection unit. One per rack. Reports on the block data segment. | COMMS (in, out) | Four (one per rack) |

4   Quantity Summary

The site section is fixed. The power-block equipment scales with the number of power blocks in the build. The AC combiner panel is the one site block whose presence depends on the build size, per its fitment rule in Section 2. Rack and BMS quantities follow from four racks per power block.

Site controller, auxiliary transformer, MV step-up transformer, revenue metering, AC collection bus: one each on every build.

Per power block: one PCS, one DC combiner, four battery racks, four rack BMS.

AC combiner panel: present only when the number of power blocks exceeds the AC collection bus feeder count.